## Slide 3
Webinar Notes
  Please use the Q & A utility to ask us any questions concerning
  the material being presented.
  Please contact Brittany Socha- chat line or email brittany.socha@arisafety.com if you would like a copy of the presentation.

## Slide 4: Previous Webinar Recap – The Hipot Test
Understanding the Hipot test
What is hipot test?
Hipot Test Requirements
  Test Parameters
Hipot Test Considerations and Failures
Leakage Current and Dielectric Breakdown
What is tested?
Arc Detection

## Slide 5: Ground Bond & Ground Continuity Testing Learning Objectives
Ground
Grounding of electrical products
Ground Bond
The Ground Bond Test – What is it?
Ground Continuity
The Ground Continuity Test – What is it?
Bond Vs. Continuity
Comparing the Ground Bond and Ground Continuity tests
Class I vs. Class II products
What is Ground?
Ground Bond Testing Examples
Ground Continuity Testing Examples
Ground Bond Standards Information
Ground Continuity Standards Information
Example of Ground Bond vs Ground Continuity
Notes: Important to understand what a groun

## Slide 6
Ground or “earth” can have numerous functions and meanings. The main purpose of a ground is to reduce the risk of electrical shock.
1 – http://en.wikipedia.org/wiki/Ground_%28electricity%29#mediaviewer/File:HomeEarthRodAustralia1.jpg
2 - http://www.howequipmentworks.com/physics/electricity/elec_safety/electrical_safety.html
Reference point for an electrical circuit
Second line of defense against electrical shock1
Common return path for electrical current2
What is Ground?

## Slide 7
Modern Power Distribution

## Slide 8
System or Service ground – designed to protect machines, tools and insulation.
Equipment Ground – Designed to protect operator from electrical shock hazards.
Service Ground
Equipment Ground
Ground or “Earth”
Different Functions of Ground

## Slide 9
Class I products provide electrical protection by employing basic insulation and a grounded chassis. Class II products employ a double layer of insulation so a grounded chassis is not necessary.
Class I vs. Class II Electrical Products

## Slide 10
What is Good Ground?
NFPA (National Fire Protection Agency) stipulates the NEC which is adopted in all 50 U.S. States. The NEC gives requirements for grounding products and installations. The NEC defines a “good” ground.
National Electrical Code
NEC 250-45
NEC 250-51
NFPA 70
Protect people and property from electrical hazards
”Any exposed non-current carrying metal parts of cord & plug connected equipment which may become energized shall be grounded.”
Permanent and Continuous
Capacity to conduct fault current
Low impedance to limit voltage to ground.

## Slide 11
Purpose
• Ground Bond and Ground Continuity tests are designed to “check” the ground connection on a product or system.
• How you ensure you have a proper ground.
Ground Bond and Continuity Tests
Method
• Apply a current to the ground point of a product or system.
• Measure potential drop across the ground circuit and calculate the circuit resistance.
Testing
• Ground Bond are generally TYPE TESTS.
• Ground Continuity are generally PRODUCTION TESTS.
These two types of tests are used to prove and verify that there is a low impedance path to the ground for electrical products and systems. This ensures proper grounding.

## Slide 12
Associated Research Inc. HYAMP connected to
a DUT (Device Under Test)
The Ground Bond Test

## Slide 13
Ground Bond Testing

## Slide 14
Ground Bond Testing

## Slide 15
Ground Bond Testing

## Slide 16
By the Numbers – What the Standards State
IEC/UL 60601-1 3rd Edition

## Slide 17
Poll Question 1

## Slide 18
By the Numbers – What the Standards State
UL 1598/CSA C22.2 No. 250.0-08
3rd Edition - Luminaires

## Slide 19
By the Numbers – What the Standards State
IEC/UL 60335-1 5th Edition

## Slide 20
Ground Continuity Testing
Definition
• A DC low current test to check circuit resistance.
• Similar concept to the Ground Bond testing.
Ground Continuity testing is the same concept as Ground Bond testing. You’re simply checking for a continuous path on a ground circuit. However, there are key differences between these two tests.
Method
• Not all readings display an Ohmic value.
• Light/buzzer meters to check whether continuity exists.

## Slide 21
By the Numbers – What the Standards State
IEC/UL 61010-1 3rd Edition

## Slide 22
By the Numbers – What the Standards State
IEC/UL 60335-1 5th Edition

## Slide 23: Ground Bond Vs. Ground Continuity
The Ground Bond test is more stringent than the Ground Continuity test.
Ground Continuity Test | Ground Bond Test
• Verifies the existence of a ground connection • Readings generally given in Ωs • The test is quick to set up and easy to perform • Usually used as an extra feature during the Hipot test. | • Verifies the integrity of a ground connection • Readings generally given in mΩ • Provides more valuable safety information about DUT • Can be combined with a Hipot test for a more complete safety testing system.

## Slide 24: Ground Bond Vs. Ground Continuity
Example: 64 strand wire with all but one strand connected.

## Slide 25: Ground Bond Vs. Ground Continuity
Example: 64 strand wire with all but one strand connected. A ground continuity test would pass this wire because the instrument reads a continuous path.

## Slide 26: Ground Bond Vs. Ground Continuity
Example: A Ground Bond test load the wire with high current. This would “burn up” the connection and cause a FAIL.

## Slide 27
Poll Question 2

## Slide 28
Ground Bond Testing Video Demonstration

## Slide 29: Summary: Ground Bond Vs. Ground Continuity
Ground
Grounding of electrical products
Ground Bond
The Ground Bond Test – What is it?
Ground Continuity
The Ground Continuity Test – What is it?
Bond Vs. Continuity
Comparing the Ground Bond and Ground Continuity tests
Class I vs. Class II products
What is Ground?
Ground Bond Testing Examples
Ground Continuity Testing Examples
Ground Bond Standards Information
Ground Continuity Standards Information
Example of Ground Bond vs Ground Continuity
Notes: Important to understand what a groun

## Slide 30
JOIN US FOR OUR NEXT WEBINAR
Wednesday, July 12 at 10AM CST (GMT – 6:00) Audit Survival Guide
Click the link in chat box to learn more
Notes: Insert next webinar info here

## Slide 31
Contact Us
If you would like a copy of this presentation please email Brittany Socha at brittany.socha@arisafety.com
Check out our website for more information arisafety.com